## 085-A-PID-00003-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Mohamed Ayyash | Add Note 10 indication here also
2 | Callout | 1 | Mohamed Ayyash | Add Note 10 indication here also
3 | Callout | 1 | Mohamed Ayyash | Add Note 10 indication here also
4 | Cloud+ | 1 | 986131 | Add the notes also on the P&ID.
5 | Text Box | 1 | alexis.martinez | GENERAL: As per Symbology BMPS-A-50003, all the Pits will show inside the word "PIT"
6 | Callout | 1 | alexis.martinez | GENERAL: Increase the size of the filled circles on field bus signal. This shall be as bigger as the circles in software signal.
7 | Call-out | 1 | A.Jabbar Mahmood | MAIN COOLING ......
8 | Callout | 1 | alexis.martinez | On note 3 add "Flat side to be located at the Top"
9 | Call-out | 1 | 986131 | reducer not shown on the P&ID. Please add.
10 | Call-out | 1 | 986131 | Refer to symbology sheet for buried pipe and use the correct line representation.
11 | Cloud+ | 1 | A.Jabbar Mahmood | SHALL READ "CW BLOWDOWN TO LSFO COOLING TOWER"
12 | Cloud+ | 1 | A.Jabbar Mahmood | SHALL READ "CW TO MAIN CW SIDE STREAM FILTERS PACKAGE U0002"
13 | Call-out | 1 | A.Jabbar Mahmood | SHALL READ AS "CW TO NON OXIDIZING BIOCIDE INJECTION PACKAGE U0012"
14 | Callout | 1 | alexis.martinez | Shows as eccentric the reducers 66"x54" in pump suction as per note 4
15 | Callout | 1 | alexis.martinez | The note 15 also applies to Sonic Flowmeter which to be located in a PIT.
16 | Callout | 1 | alexis.martinez | The note 15 also applies to Sonic Flowmeter which to be located in a PIT.
17 | Cloud+ | 1 | Khalid | To U0012