## 085-A-PID-00005-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Callout | 1 | Mohamed Ayyash | Add Note 10 indication here also
2 | Callout | 1 | Mohamed Ayyash | Add Note 10 indication here also
3 | Callout | 1 | alexis.martinez | On note 3 add "Flat side to be located at the Top"
4 | Call-out | 1 | A.Jabbar Mahmood | SECONDARY COOLING ......
5 | Cloud+ | 1 | A.Jabbar Mahmood | SHALL READ "CW TO SECONDARY CW SIDE STREAM FILTERS PACKAGE U0003"
6 | Call-out | 1 | A.Jabbar Mahmood | SHALL READ AS "CW TO NON OXIDIZING BIOCIDE INJECTION PACKAGE U0013"
7 | Cloud+ | 1 | 986131 | Show these notes on the P&ID also.
8 | Callout | 1 | alexis.martinez | Shows as eccentric the reducers 66"x54" in pump suction as per note 4
9 | Callout | 1 | alexis.martinez | The note 15 also applies to Sonic Flowmeter which to be located in a PIT.
10 | Cloud+ | 1 | Khalid | To U0013
11 | Call-out | 1 | A.Jabbar Mahmood | TR to clarify the rationale for the differences between the blowdown system of the MAIN CW and SECONDARY CW. In here, an XV downstream of the main Control valve is provided while for the MAIN CW blowdown, another FV is provided upstream of the main FV with link the to conductivity controller.