## 085-A-PID-00006-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | 986131 | Add the Equipment Data Blocks. If details are not available then a hold can be used against each such parameter.
2 | Call-out | 1 | Abdulaziz | Fan G.Box and motor vibration shall be connected to MMS for monitoring and protection. Applicable for all CWT Fans.
3 | Call-out | 1 | Abdulaziz | Fan G.Box low oil level cut off switch to be shown. Applicable for all CWT Fans.
4 | Call-out | 1 | Abdulaziz | Typo :To be corrected and re phrased as FAN MOTOR GEAR LUBRICATION OIL TEMPERATURE.