## 085-A-PID-00007-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Call-out | 1 | 986131 | Isolation valve with minimum distance from the branch point required. Comment also applies to 085-A-PID-0008-001 085-A-PID-0009-001 085-A-PID-0010-001
2 | Call-out | 1 | 986131 | Refer P&ID 085-A-PID-0008-001 085-A-PID-0009-001 085-A-PID-0010-001 The eccentric reducer is put in the reverse way. Please correct as appropriate. Do we need a eccentric reducer in this service?
3 | Call-out | 1 | 986131 | Review the requirement of a pressure input from turbine discharge to set the temperature target. Comment also applies to 085-A-PID-0008-001 085-A-PID-0009-001 085-A-PID-0010-001
4 | Call-out | 1 | Abdulaziz | Standard tagging format to be followed
5 | Call-out | 1 | 986131 | Weep hole to have a hard pipe to the ground for safe disposal of any hot water. Similar to that shown on RV0034 outlet. Also applies to other similar location. Comment also applies to 085-A-PID-0008-001 085-A-PID-0009-001 085-A-PID-0010-001