## 085-A-PID-00010-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | alexis.martinez | GENERAL: The expansion used at the RV discharge should a concentric expansion.
2 | Callout | 1 | alexis.martinez | On RV-0029 and RV-0045, the reduction at the discharge is 3"x0". Correct reduction size based on RV size
3 | Callout | 1 | alexis.martinez | On RV-0030 the reduction at the discharge is 18"x0". Correct reduction size based on RV size
4 | Call-out | 1 | Abdulaziz | Standard tagging format to be followed