## 085-A-PID-00013-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Abdulaziz | All equipment that are close to the cooling tower structure shall be provided with shelter to protect them against water evaporation and drift water droplets.
2 | Call-out | 1 | Abdulaziz | Blower bearings vibration and temperature monitoring shall be shown.
2 | Call-out | 1 | A.Jabbar Mahmood | P0001A/B/C/D/E
4 | Cloud+ | 1 | 986131 | Please review the requirement to add a symbol for concrete channel and add it to BMPS-50003.