## 085-L-PPN-00001-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 |  | 1 | AutoCAD SHX Text | - C/Arapiles 14, Madrid, Spain
2 | Callout | 1 | Erwin.Lugue | Refer to requirements in BMPS-S5 sec 6.7
3 | Call-out | 1 | MAK | 085 - COOLING WATER TOWER
4 | Text Box | 1 | Ahmed Marhoon | 1. All instruments located at pits shall be safely accessible and readable from outside the pits. Contractor to consider the required spacings. 2. Analyzers if not installed in ventilated analyzer house, shall be installed in field shelters. Contractor to consider space for these analyzers with the necessary access in the plot plan. 3. Contractor to ensure that underground cable trench size and design is adequate to accommodate all the underground multipair cables with the necessary segregation from high voltage electrical trenches and 30% spare space for future use as per the BMPS-J series. Any deviation from this requirement shall be brought to owner's attention for review/evaluation.
5 | Call-out | 1 | Abdulaziz | 1. All measures shall be taken in to account to prevent ground water seepage. 2. Pump baseplate and associated pipe support shall be coated with corrosion re-sistance paint. 3. Pump pit room shall be furnished with pump out facility in case of any water leakage.
6 | Cloud+ | 1 | 986131 | Acid and alkali are not compatible material, review the need to segregate the handling area.
7 | Callout | 1 | Berik.Nurbolatov | All equipments should be shown in section view for more reference. Please dimensions and distances.
8 | Callout | 1 | Robert.Kawitzki | At what point does the pipe rack add another tier?
9 | Callout | 1 | Erwin.Lugue | Bundwall? Clarify solid lines.
10 | Call-out | 1 | MAK | Change L to A which is the correct Material Class for Plot Plan.
11 | Callout | 1 | Robert.Kawitzki | Consider path of power supply to motors. Cannot approach from UG if area is bunded
12 | Callout | 1 | Berik.Nurbolatov | Contractor to follow the requirements given on BMPS-L3, Section 6.1.3 equipment and equipment structures shall be arranged to permit planned maintenance by means of mobile maintenance equipment without blocking accessways.
13 | Text Box | 1 | Erwin.Lugue | corresponds
14 | Callout | 1 | Erwin.Lugue | Curb? Verify requirement for spill control or containment
15 | Call-out | 1 | MAK | CWT
16 | Call-out | 1 | MAK | Delete U and never use prefixes for Unit Nos.
17 | Call-out | 1 | MAK | Delete. This is for Bapco use.
18 | Callout | 1 | Erwin.Lugue | Elevations missing- typ comment
19 | Call-out | 1 | 986131 | Ensure adequate access is provide to remove and add the caustic Isotanks.
20 | Call-out | 1 | 986131 | Ensure adequate Access to replace the daughter tanks for U0005,6&7
21 | Call-out | 1 | 986131 | Ensure adequate arrangement is in place to fill H2SO4 tank.
22 | Callout | 1 | Robert.Kawitzki | Ensure that the bellows will be accessible and no valves are under the rack
23 | Text Box | 1 | Sameer Foujdar | Equipment numbers to be checked and correctly marked in the plot plan as per the new numbering system.
24 | Call-out | 1 | Sameer Foujdar | Equipment numbers to be marked.
25 | Call-out | 1 | Sameer Foujdar | Equipment numbers to be marked.
26 | Text Box | 1 | Erwin.Lugue | Finished floor level?
27 | Text Box | 1 | RASHED SHOWAITER | FOR T&Is: TO SHOW LAYDOWN AREA FOR LOUVERS, FAN STACK, DISTRIBUTORS, SPRAY NOZZLES, CORRUGATED CASING PANEL, PACKING, ETC.
28 | Text Box | 1 | MAK | General Comment: The latest drawing borders have been submitted to JV Directorate on April 2018. Please use the latest drawing borders that are part of the Homogenisation Procedure.
29 | Call-out | 1 | MAK | General Comment: Use DD.MM.YYYY format for the date, e.g. 25.05.2018
30 | Callout | 1 | Berik.Nurbolatov | GENERAL:Please arrange distance data b/ n grids , units
31 | Callout | 1 | Robert.Kawitzki | I assume this is a pipe bridge? Show a side elevation
32 | Call-out | 1 | 986131 | In order to allow maintenance/shutdown of primary cooling tower while the secondary cooling tower is in operation or vice versa. A physical separation may be required between primary and secondary towers. Please review the plot plan from a maintenance point of view. Something similar to the attached photo.
33 | Callout | 1 | Erwin.Lugue | Include all symbologies & abbreviations
34 | Callout | 1 | Bernard.Grace | Include the nearest Survey Control Stations/Monuments to aid setting out and construction within the plot plan
35 | Callout | 1 | Erwin.Lugue | Indicate access & ramps (if required)
36 | Callout | 1 | Robert.Kawitzki | Is this area large enough to provide a laydown area for a fan blade without blocking the access road?
37 | Callout | 1 | Erwin.Lugue | Locate location of ladders to access cooling tower fans
38 | Callout | 1 | Erwin.Lugue | Location?
39 | Callout | 1 | Erwin.Lugue | Location?
40 | Callout | 1 | Erwin.Lugue | Location?
41 | Callout | 1 | Erwin.Lugue | Location?
42 | Call-out | 1 | Abdulaziz | Lube oil rack for Fan G.Box oil can shall be provided at three location at least
43 | Callout | 1 | Erwin.Lugue | Missing grid frame designations, dimensions, & location of expansion joints
44 | Callout | 1 | Erwin.Lugue | Missing coordinates, levels of road intersections- typ. comments
45 | Text Box | 1 | Erwin.Lugue | Missing dimensions, coordinates for locating positions of equipments & structures
46 | Text Box | 1 | Erwin.Lugue | Missing eyewash locations
47 | Text Box | 1 | Erwin.Lugue | Missing firefighting facilities, i.e. sand bins, hydrants, firehose reels, monitors, etc.
48 | Text Box | 1 | Erwin.Lugue | Missing location of guardposts, crash barriers, chain barricades, etc.
49 | Callout | 1 | Erwin.Lugue | Missing section & dimension of the platform- typ. comment
50 | Callout | 1 | Erwin.Lugue | Missing shelters for lube storage & chemical storage as per BPMS vol 2 sec 6, sub sec 6.3.3
51 | Text Box | 1 | Erwin.Lugue | Missing street/plant lighting layout
52 | Call-out | 1 | Abdulaziz | Monkey ladder shall be replaced with stairway for safe ascending and descending specially with maintenance activities that involves tools handling
53 | Text Box | 1 | RASHED SHOWAITER | NEED TO ILLUSTRATE THE CRANE PARKING FOR T&Is
54 | Callout | 1 | Erwin.Lugue | No details & elevation for this structure
55 | Cloud+ | 1 | Abdulaziz | No reference for the OMG on th plot plan
56 | Callout | 1 | Erwin.Lugue | No structure tag/ designation
57 | Callout | 1 | Erwin.Lugue | No structure tag/ designation
58 | Callout | 1 | Erwin.Lugue | Platform with spill control? Clarify
59 | Callout | 1 | Berik.Nurbolatov | Please ensure that 3 off decimals are used ..e.g 14.750
60 | Callout | 1 | Berik.Nurbolatov | please include equipments 085PLF......into Equipment List, with description.
61 | Callout | 1 | Berik.Nurbolatov | Please mention HPP EL. relative to the site datum.
62 | Text Box | 1 | Ahmed Ali | please refer to 7CDU plot plan comments regarding the requirement of oil and chemical shelter.
63 | Callout | 1 | Berik.Nurbolatov | Plot plans shall be dimensioned in metric units (mm) of linear measurement (refer BMPS A8 ‘General guidelines of Plot plan layout Part B Appendix B1
64 | Callout | 1 | Robert.Kawitzki | Provide tie steel at top of rack
65 | Callout | 1 | Robert.Kawitzki | Provide turn in radius for approach roads - typical comment
66 | Callout | 1 | Berik.Nurbolatov | Rack grids should be numbered and shown in appropriate manner.
67 | Callout | 1 | Erwin.Lugue | Refer to BMP-CON-LET-00047
68 | Text Box | 1 | Erwin.Lugue | relative
69 | Text Box | 1 | Erwin.Lugue | relative
70 | Text Box | 1 | Robert.Kawitzki | Section
71 | Cloud+ | 1 | 986131 | Show 085K0001A/B and K0002A/B on plot plan.
72 | Callout | 1 | Robert.Kawitzki | Show access platforms
73 | Callout | 1 | Robert.Kawitzki | Show dotted discharge piping to allow for maintenance access
74 | Callout | 1 | Robert.Kawitzki | Show support steel for feed lines. Cannot be supported of cooling tower
75 | Callout | 1 | Erwin.Lugue | Sloped? Show in plan
76 | Text Box | 1 | Erwin.Lugue | Sloped? Show in plan
77 | Callout | 1 | Erwin.Lugue | Specify bottom elevation of pits & basins in plans
78 | Callout | 1 | Erwin.Lugue | Specify bottom elevation of pits & basins in plans
79 | Callout | 1 | Erwin.Lugue | Spill control? Clarify lines
80 | Callout | 1 | Erwin.Lugue | Spill control? Clarify lines
81 | Callout | 1 | Robert.Kawitzki | State the width of the approach road. Min width shall be 4m
82 | Call-out | 1 | Mahdi Ali | Text shall be aligned
83 |  | 1 | AutoCAD SHX Text | The present document or drawing is property of TECHNIP ITALY S.p.A. and shall not, under any circumstances, be totally or partially, directly or indirectly, transferred, reproduced, copied, disclosed or used, without its prior written consent, for any purpose and in any way other than that for which it is specifically furnished or outside the extent of the agreed upon right of use.
84 | Callout | 1 | Berik.Nurbolatov | The requirement of walking distance ( Section 7.1.7, BMPS-L3 )should be considered when arranging access.
85 | Callout | 1 | Robert.Kawitzki | This platform is blocking maintenance access for pumps
86 | Text Box | 1 | Erwin.Lugue | To provide manual lifting hoists or monorail for maintenance of main & secondary basins- FEED reqt.
87 | Call-out | 1 | Abdulaziz | To provide sufficient accesses to thew CWT fan platform as per the codes.
88 | Callout | 1 | Erwin.Lugue | TOC level?
89 | Text Box | 1 | MAK | TOWER
90 | Text Box | 1 | Abdulaziz | TR to ensure easy access to perform any maintenance activities for the pump.
91 | Call-out | 1 | Mahdi Ali | Use EPC drawing number rather than FEED drawing number
92 | Call-out | 1 | Ahmed Ali | use the correct unit name Cooling Water Tower
93 | Callout | 1 | Erwin.Lugue | Verify finished floor elevation
94 | Callout | 1 | Robert.Kawitzki | What are these platforms for? Do NOT place valves or bellows under the rack
95 | Callout | 1 | Robert.Kawitzki | What are these platforms used for? Show dotted outlines for serviced equipment with a note so this makes sense
96 | Callout | 1 | Robert.Kawitzki | What does this shape signify?
97 | Callout | 1 | Erwin.Lugue | Where it refers to?
98 | Callout | 1 | Robert.Kawitzki | Why are different tier heights used? Stick with 2000 or 2500
99 | Callout | 1 | Robert.Kawitzki | Why is this rack this far east?