## 085-S-DAT-00014-001-RA
ID | Subject | Page | Author | Comments | JV Replies | Comment included (Y/N) | Bapco closure (Y/N)
1 | Text Box | 1 | Ahmed Marhoon | Comments related to instrumentation and control scope have been provided on the previous revision and need to be implemented. JV replies on respective comments attached to this transmittal did not adequately address the intent of the comments. Proper justification needs to be provided to the owner for not implementing the comments.
2 | Text Box | 1 | MAK | Use the latest document template which is part of the Homogenization Procedure. MOC Contractor shall coordinate with JV Directorate.
3 | Text Box | 1 | Mahdi Ali | Why this document is classified as DAT??
4 | Text Box | 3 | Omran A | /PLC
5 | Call-out | 3 | Abdulaziz | Air blowers are essential for operation of this package therefore, MCM shall be considered to monitoring and protection.
6 | Call-out | 3 | Abdulaziz | All effort tin making the system easy to maintained shall be considered specifically with multiple filters and when operation intervention is required
7 | Cloud+ | 3 | Mohamed Ayyash | Correct, should read Tower not Unit.
8 | Cloud+ | 3 | Mohamed Ayyash | Delete "u" from uniy number
9 | Call-out | 3 | Abdulaziz | To ensure the optimum level of integrity for the filters system and air blowers. In addition, further details related to regular preventative maintenance and spares required to be established and forwarded for review and comments.
10 | Cloud+ | 4 | Mohamed Ayyash | Align
11 | Cloud+ | 4 | Mohamed Ayyash | CWT means Cooling Water Tower ?
12 | Callout | 7 | Fernando.Perez | Should be number of cartridge (Flters are 8 nos)
13 | Text Box | 8 | Omran A | Basis the following, the classification of the Instrument/control system will be decided: "Once Hazardous Area Classification (HAC) of each area/plant" and "final location of the instrumentations and Control Systems are finalized".
14 | Call-out | 8 | 986131 | Filter media life to be guaranteed. This will govern the maintenance cycle, unless the filters life is 6 years (T&I time).
15 | Callout | 8 | Fernando.Perez | Include IP enclosure
16 | Cloud+ | 8 | 986131 | review these numbers, the addition of checmical , i.e. Bio dispersant, Oxidizing biocide, non - oxidizing bio sides etc. would increase the TDS and Chloride. Current numbers quoted do not account for this.
17 | Callout | 10 | Yousif Ahmadi | Equipment gauging sketch with initial gauging
18 | Call-out | 10 | 986131 | Including maintenance platforms
19 | Text Box | 11 | Abdulaziz | Shelters/shield shall be considerer to protect the surrounding equipment and facility against the harsh environment nearby the cooling tower that is cause by drift droplets of water evaporation. It is also important to consider all climate aspects like wind direction when choosing the location of the package.
20 | Cloud+ | 12 | Mohamed Ayyash | Typo. Move the letter "e" back in place
21 | Call-out | 14 | 986131 | ADD: 000-S-MRQ-70001-001
22 | Text Box | 14 | Mahdi Ali | Use Bapco numbers